## Main List
WattNode MODBUS Register List
Firmware Version: 18 |  |  | Date: 2011-11-30 |  |  | Changes since ver. 12 are highlighted green
Basic Registers - Floating Point
| Registers | Name | Units | Access | Default | Description
Energy Registers
| 1001, 1002 | EnergySum | kWh | Read/Write |  | Total net (bidirectional) energy
| 1003, 1004 | EnergyPosSum | kWh | Read/Write |  | Total positive energy
| 1005, 1006 | EnergySumNR | kWh | Read-Only |  | Total net (bidirectional) energy - non resettable
| 1007, 1008 | EnergyPosSumNR | kWh | Read-Only |  | Total positive energy - non resettable
Power Registers
| 1009, 1010 | PowerSum | W | Read-Only |  | Real power, sum of active phases
| 1011, 1012 | PowerA | W | Read-Only |  | Real power, phase A
| 1013, 1014 | PowerB | W | Read-Only |  | Real power, phase B
| 1015, 1016 | PowerC | W | Read-Only |  | Real power, phase C
Voltage Registers
| 1017, 1018 | VoltAvgLN | V | Read-Only |  | Average phase-to-neutral voltage
| 1019, 1020 | VoltA | V | Read-Only |  | RMS voltage, phase A to neutral
| 1021, 1022 | VoltB | V | Read-Only |  | RMS voltage, phase B to neutral
| 1023, 1024 | VoltC | V | Read-Only |  | RMS voltage, phase C to neutral
| 1025, 1026 | VoltAvgLL | V | Read-Only |  | Average line-to-line voltage
| 1027, 1028 | VoltAB | V | Read-Only |  | RMS voltage, line-to-line, phase A to B
| 1029, 1030 | VoltBC | V | Read-Only |  | RMS voltage, line-to-line, phase B to C
| 1031, 1032 | VoltAC | V | Read-Only |  | RMS voltage, line-to-line, phase A to C
Frequency Register
| 1033, 1034 | Freq | Hz | Read-Only |  | Power line frequency
Basic Registers - Integer
| Registers | Name | Units | Access | Default | Description
Energy Registers
| 1201, 1202 | EnergySum | 0.1 kWh | Read/Write |  | Total net (bidirectional) energy
| 1203, 1204 | EnergyPosSum | 0.1 kWh | Read/Write |  | Total positive energy
| 1205, 1206 | EnergySumNR | 0.1 kWh | Read-Only |  | Total net (bidirectional) energy - non resettable
| 1207, 1208 | EnergyPosSumNR | 0.1 kWh | Read-Only |  | Total positive energy - non resettable
Power Registers
| 1209 | PowerSum | PowerIntScale | Read-Only |  | Real power, sum of active phases
| 1210 | PowerA | PowerIntScale | Read-Only |  | Real power, phase A
| 1211 | PowerB | PowerIntScale | Read-Only |  | Real power, phase B
| 1212 | PowerC | PowerIntScale | Read-Only |  | Real power, phase C
Voltage Registers
| 1213 | VoltAvgLN | 0.1 V | Read-Only |  | Average phase-to-neutral voltage
| 1214 | VoltA | 0.1 V | Read-Only |  | RMS voltage, phase A to neutral
| 1215 | VoltB | 0.1 V | Read-Only |  | RMS voltage, phase B to neutral
| 1216 | VoltC | 0.1 V | Read-Only |  | RMS voltage, phase C to neutral
| 1217 | VoltAvgLL | 0.1 V | Read-Only |  | Average line-to-line voltage
| 1218 | VoltAB | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase A to B
| 1219 | VoltBC | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase B to C
| 1220 | VoltAC | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase A to C
Frequency Register
| 1221 | Freq | 0.1 Hz | Read-Only |  | Power line frequency
Advanced Registers - Floating Point
| Registers | Name | Units | Access | Default | Description
Energy Registers
| 1101, 1102 | EnergyA | kWh | Read/Write |  | Net (bidirectional) energy, phase A
| 1103, 1104 | EnerygB | kWh | Read/Write |  | Net (bidirectional) energy, phase B
| 1105, 1106 | EnergyC | kWh | Read/Write |  | Net (bidirectional) energy, phase C
| 1107, 1108 | EnergyPosA | kWh | Read/Write |  | Positive energy, phase A
| 1109, 1110 | EnergyPosB | kWh | Read/Write |  | Positive energy, phase B
| 1111, 1112 | EnergyPosC | kWh | Read/Write |  | Positive energy, phase C
| 1113, 1114 | EnergyNegSum | kWh | Read/Write |  | Negative energy, sum of active phases
| 1115, 1116 | EnergyNegSumNR | kWh | Read-Only |  | Negative energy, sum of active phases - non resettable
| 1117, 1118 | EnergyNegA | kWh | Read/Write |  | Negative energy, phase A
| 1119, 1120 | EnergyNegB | kWh | Read/Write |  | Negative energy, phase B
| 1121, 1122 | EnergyNegC | kWh | Read/Write |  | Negative energy, phase C
| 1123, 1124 | EnergyReacSum | kVARh | Read/Write |  | Reactive energy, sum of active phases
| 1125, 1126 | EnergyReacA | kVARh | Read/Write |  | Net reactive energy, phase A
| 1127, 1128 | EnergyReacB | kVARh | Read/Write |  | Net reactive energy, phase B
| 1129, 1130 | EnergyReacC | kVARh | Read/Write |  | Net reactive energy, phase C
| 1131, 1132 | EnergyAppSum | kVAh | Read/Write |  | Apparent energy, sum of active phases
| 1133, 1134 | EnergyAppA | kVAh | Read/Write |  | Apparent energy, phase A
| 1135, 1136 | EnergyAppB | kVAh | Read/Write |  | Apparent energy, phase B
| 1137, 1138 | EnergyAppC | kVAh | Read/Write |  | Apparent energy, phase C
Power Factor Registers
| 1139, 1140 | PowerFactorAvg |  | Read-Only |  | Power factor, average of active phases
| 1141, 1142 | PowerFactorA |  | Read-Only |  | Power factor, phase A
| 1143, 1144 | PowerFactorB |  | Read-Only |  | Power factor, phase B
| 1145, 1146 | PowerFactorC |  | Read-Only |  | Power factor, phase C
Reactive and Apparent Power Registers
| 1147, 1148 | PowerReacSum | VAR | Read-Only |  | Reactive power, sum of active phases
| 1149, 1150 | PowerReacA | VAR | Read-Only |  | Reactive power, phase A
| 1151, 1152 | PowerReacB | VAR | Read-Only |  | Reactive power, phase B
| 1153, 1154 | PowerReacC | VAR | Read-Only |  | Reactive power, phase C
| 1155, 1156 | PowerAppSum | VA | Read-Only |  | Apparent power, sum of active phases
| 1157, 1158 | PowerAppA | VA | Read-Only |  | Apparent power, phase A
| 1159, 1160 | PowerAppB | VA | Read-Only |  | Apparent power, phase B
| 1161, 1162 | PowerAppC | VA | Read-Only |  | Apparent power, phase C
Current Registers
| 1163, 1164 | CurrentA | A | Read-Only |  | RMS current, phase A
| 1165, 1166 | CurrentB | A | Read-Only |  | RMS current, phase B
| 1167, 1168 | CurrentC | A | Read-Only |  | RMS current, phase C
Demand Registers
| 1169, 1170 | Demand | W | Read-Only |  | Real power demand averaged over the demand period
| 1171, 1172 | DemandMin | W | Read-Only |  | Minimum power demand
| 1173, 1174 | DemandMax | W | Read-Only |  | Maximum power demand
| 1175, 1176 | DemandApp | W | Read-Only |  | Apparent power demand
| 1177, 1178 | DemandA | W | Read-Only |  | Real power demand, phase A
| 1179, 1180 | DemandB | W | Read-Only |  | Real power demand, phase B
| 1181, 1182 | DemandC | W | Read-Only |  | Real power demand, phase C
Advanced Registers - Integer
| Registers | Name | Units | Access | Default | Description
Energy Registers
| 1301, 1302 | EnergyA | 0.1 kWh | Read/Write |  | Net energy, phase A
| 1303, 1304 | EnerygB | 0.1 kWh | Read/Write |  | Net energy, phase B
| 1305, 1306 | EnergyC | 0.1 kWh | Read/Write |  | Net energy, phase C
| 1307, 1308 | EnergyPosA | 0.1 kWh | Read/Write |  | Positive energy, phase A
| 1309, 1310 | EnergyPosB | 0.1 kWh | Read/Write |  | Positive energy, phase B
| 1311, 1312 | EnergyPosC | 0.1 kWh | Read/Write |  | Positive energy, phase C
| 1313, 1314 | EnergyNegSum | 0.1 kWh | Read/Write |  | Negative energy, sum of active phases
| 1315, 1316 | EnergyNegSumNR | 0.1 kWh | Read-Only |  | Negative energy, sum of active phases - non resettable
| 1317, 1318 | EnergyNegA | 0.1 kWh | Read/Write |  | Negative energy, phase A
| 1319, 1320 | EnergyNegB | 0.1 kWh | Read/Write |  | Negative energy, phase B
| 1321, 1322 | EnergyNegC | 0.1 kWh | Read/Write |  | Negative energy, phase C
| 1323, 1324 | EnergyReacSum | 0.1 kVARh | Read/Write |  | Reactive energy, sum of active phases
| 1325, 1326 | EnergyReacA | 0.1 kVARh | Read/Write |  | Net reactive energy, phase A
| 1327, 1328 | EnergyReacB | 0.1 kVARh | Read/Write |  | Net reactive energy, phase B
| 1329, 1330 | EnergyReacC | 0.1 kVARh | Read/Write |  | Net reactive energy, phase C
| 1331, 1332 | EnergyAppSum | 0.1 kVAh | Read/Write |  | Apparent energy, sum of active phases
| 1333, 1334 | EnergyAppA | 0.1 kVAh | Read/Write |  | Apparent energy, phase A
| 1335, 1336 | EnergyAppB | 0.1 kVAh | Read/Write |  | Apparent energy, phase B
| 1337, 1338 | EnergyAppC | 0.1 kVAh | Read/Write |  | Apparent energy, phase C
Power Factor Registers
| 1339 | PowerFactorAvg | 0.01 | Read-Only |  | Power factor, average of active phases
| 1340 | PowerFactorA | 0.01 | Read-Only |  | Power factor, phase A
| 1341 | PowerFactorB | 0.01 | Read-Only |  | Power factor, phase B
| 1342 | PowerFactorC | 0.01 | Read-Only |  | Power factor, phase C
Reactive and Apparent Power Registers
| 1343 | PowerReacSum | PowerIntScale | Read-Only |  | Reactive power VAR, sum of active phases
| 1344 | PowerReacA | PowerIntScale | Read-Only |  | Reactive power VAR, phase A
| 1345 | PowerReacB | PowerIntScale | Read-Only |  | Reactive power VAR, phase B
| 1346 | PowerReacC | PowerIntScale | Read-Only |  | Reactive power VAR, phase C
| 1347 | PowerAppSum | PowerIntScale | Read-Only |  | Apparent power VA, sum of active phases
| 1348 | PowerAppA | PowerIntScale | Read-Only |  | Apparent power VA, phase A
| 1349 | PowerAppB | PowerIntScale | Read-Only |  | Apparent power VA, phase B
| 1350 | PowerAppC | PowerIntScale | Read-Only |  | Apparent power VA, phase C
Current Registers
| 1351 | CurrentA | CurrentIntScale | Read-Only |  | RMS current, phase A
| 1352 | CurrentB | CurrentIntScale | Read-Only |  | RMS current, phase B
| 1353 | CurrentC | CurrentIntScale | Read-Only |  | RMS current, phase C
Demand Registers
| 1354 | Demand | PowerIntScale | Read-Only |  | Real power demand averaged over the demand period
| 1355 | DemandMin | PowerIntScale | Read-Only |  | Minimum power demand
| 1356 | DemandMax | PowerIntScale | Read-Only |  | Maximum power demand
| 1357 | DemandApp | PowerIntScale | Read-Only |  | Apparent power demand
| 1358 | DemandA | PowerIntScale | Read-Only |  | Real power demand, phase A
| 1359 | DemandB | PowerIntScale | Read-Only |  | Real power demand, phase B
| 1360 | DemandC | PowerIntScale | Read-Only |  | Real power demand, phase C
| 1361 | IoPinState |  | Read/Write |  | IO pin digital input or output state
| 1362, 1363 | PulseCount |  | Read/Write |  | IO pin pulse count
Configuration Registers - Integer
| Registers | Name | Units | Access | Default | Description
| 1601, 1602 | ConfigPasscode |  | Read/Write | 0 | Optional passcode to prevent unauthorized changes to configuration
| 1603 | CtAmps | 1 A | Read/Write | 5 | Current transformer rated current
| 1604 | CtAmpsA | 1 A | Read/Write | 5 | Optional CT rated current override for phase A
| 1605 | CtAmpsB | 1 A | Read/Write | 5 | Optional CT rated current override for phase B
| 1606 | CtAmpsC | 1 A | Read/Write | 5 | Optional CT rated current override for phase C
| 1607 | CtDirections |  | Read/Write | 0 | Optionally invert CT orientations
| 1608 | Averaging |  | Read/Write | 1 (fast) | Configure measurement averaging
| 1609 | PowerIntScale | 1 W | Read/Write | 0 (auto) | Scale factor for integer power registers
| 1610 | DemPerMins | 1 minute | Read/Write | 15 | Demand period
| 1611 | DemSubints |  | Read/Write | 1 | Number of demand subintervals
| 1612 | GainAdjustA | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for phase A
| 1613 | GainAdjustB | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for phase B
| 1614 | GainAdjustC | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for phase C
| 1615 | PhaseAdjustA | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for phase A
| 1616 | PhaseAdjustB | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for phase B
| 1617 | PhaseAdjustC | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for phase C
| 1618 | CreepLimit |  | Read/Write | 1500 | Configure minimum power for a non-zero reading
| 1619 | PhaseOffset | 1 degree | Read/Write | 120 | Nominal angle between primary voltage phases (0, 60, 90, 120, or 180)
| 1620 | ZeroEnergy |  | Read/Write | - | Write 1 to zero all resettable energy registers
| 1621 | ZeroDemand |  | Read/Write | - | Write 1 to zero all demand values
| 1622 | CurrentIntScale |  | Read/Write | 20000 | Scale factor for integer current registers
| 1623 | IoPinMode |  | Read/Write | 0 | 0 = IO feature disabled 1 = Falling edge pulse counter and digital input 2 = Rising edge pulse counter and digital input 3 = Open-drain output restores state at power-up 4 = Open-drain output goes low at power-up 5 = Open-drain output goes high at power-up 6 = Push-pull output restores state at power-up 7 = Push-pull output goes low at power-up 8 = Push-pull output goes high at power-up
Communication Registers
| Registers | Name | Units | Access | Default | Description
| 1651 | ApplyComConfig |  | Read/Write | 0 | Writing 1234 applies the configuration settings below. Reads 1 if changes not applied yet.
| 1652 | Address |  | Read/Write | 0 | MODBUS address (if non-zero, overrides DIP switches)
| 1653 | BaudRate |  | Read/Write | 0 | 0 = DIP Switch Assigned 4 = 9600 baud 5 = 19200 baud 6 = 38400 baud
| 1654 | ParityMode |  | Read/Write | 0 | 0 = N81 (no parity, one stop bit) 1 = E81 (even parity, one stop bit)
| 1655 | ModbusMode |  | Read/Write | 0 | 0=RTU 1=TCP-RTU
| 1656 | ReplyDelay |  | Read/Write | 5 | Minimum Modbus reply delay. 5 to 180 ms
Customer Diagnostic Registers - Integer
| Registers | Name | Units | Access | Default | Description
| 0001, 0002 | DummyReg |  | Read-Only |  | Dummy register; always returns zero; can be used to scan for active MODBUS addresses
| 1701, 1702 | SerialNumber |  | Read-Only |  | The unique WattNode serial number
| 1703, 1704 | UptimeSecs | Seconds | Read-Only |  | Time in seconds since last power on
| 1705, 1706 | TotalSecs | Seconds | Read-Only |  | Total seconds of operation
| 1707 | Model |  | Read-Only |  | Encoded WattNode model
| 1708 | Version |  | Read-Only |  | Firmware version
| 1709 | Options |  | Read-Only |  | WattNode options
| 1710 | ErrorStatus | n.a. | Read/Write |  | List of recent errors and events
| 1711 | PowerFailCount |  | Read/Write |  | Power failure count
| 1712 | CrcErrorCount |  | Read/Write |  | Count of MODBUS CRC communication errors
| 1713 | FrameErrorCount |  | Read/Write |  | Count of MODBUS framing errors
| 1714 | PacketErrorCount |  | Read/Write |  | Count of bad MODBUS packets
| 1715 | OverrunCount |  | Read/Write |  | Count of MODBUS buffer overruns
| 1716 | ErrorStatus1 | n.a. | Read/Write |  | Newest error or event (0 = no errors)
| 1717 | ErrorStatus2 | n.a. | Read/Write |  | Next oldest error or event
| 1718 | ErrorStatus3 | n.a. | Read/Write |  | Next oldest error or event
| 1719 | ErrorStatus4 | n.a. | Read/Write |  | Next oldest error or event
| 1720 | ErrorStatus5 | n.a. | Read/Write |  | Next oldest error or event
| 1721 | ErrorStatus6 | n.a. | Read/Write |  | Next oldest error or event
| 1722 | ErrorStatus7 | n.a. | Read/Write |  | Next oldest error or event
| 1723 | ErrorStatus8 | n.a. | Read/Write |  | Oldest error or event
Note on E7: Before version 16, this was Read-Only
Note on E8: Before version 16, this was Read-Only
Note on E31: Before version 16, this was Read-Only
Note on E32: Before version 16, this was Read-Only
Note on E55: Before version 16, this was Read-Only
Note on E56: Before version 16, this was Read-Only
Note on E57: Before version 16, this was Read-Only
Note on E58: Before version 16, this was Read-Only
Note on E59: Before version 16, this was Read-Only
Note on E60: Before version 16, this was Read-Only
Note on E61: Before version 16, this was Read-Only
Note on E63: Before version 16, this was Read-Only
Note on E64: Before version 16, this was Read-Only
Note on E65: Before version 16, this was Read-Only
Note on E66: Before version 16, this was Read-Only
Note on E67: Before version 16, this was Read-Only
Note on E68: Before version 16, this was Read-Only
Note on E69: Before version 16, this was Read-Only
Note on E70: Before version 16, this was Read-Only
Note on E71: Before version 16, this was Read-Only
Note on E72: Before version 16, this was Read-Only
Note on E73: Before version 16, this was Read-Only
Note on B97: Register added on version 16
Note on B98: Register added on version 16
Note on B99: Register added on version 16
Note on E104: Before version 16, this was Read-Only
Note on E105: Before version 16, this was Read-Only
Note on E106: Before version 16, this was Read-Only
Note on E107: Before version 16, this was Read-Only
Note on E108: Before version 16, this was Read-Only
Note on E109: Before version 16, this was Read-Only
Note on E110: Before version 16, this was Read-Only
Note on E112: Before version 16, this was Read-Only
Note on E113: Before version 16, this was Read-Only
Note on E114: Before version 16, this was Read-Only
Note on E115: Before version 16, this was Read-Only
Note on E116: Before version 16, this was Read-Only
Note on E117: Before version 16, this was Read-Only
Note on E118: Before version 16, this was Read-Only
Note on E119: Before version 16, this was Read-Only
Note on E120: Before version 16, this was Read-Only
Note on E121: Before version 16, this was Read-Only
Note on E122: Before version 16, this was Read-Only
Note on B146: Register added on version 16
Note on B147: Register added on version 16
Note on B148: Register added on version 16
Note on B149: Register added on version 16
Note on E149: Can only be written when the IO pin is configured as an output (in modes 3 to 8)
Note on B150: Register added on version 16
Note on E155: On version 16, this assigns the same value to all 3 per-phase CtAmps registers when written. It reads zero unless all three per-phase CtAmps registers are the same, in which case it reads back that value.
Note on F156: Before version 16, this defaulted to zero.
Note on F157: Before version 16, this defaulted to zero.
Note on F158: Before version 16, this defaulted to zero.
Note on G171: Before version 16 only 0, 120 and 180 were allowed.
Note on B174: Register added on version 16
Note on B175: Register added on version 16
Note on B184: Register added on version 16

## Flattened
index | Group | Subgroup | Registers | Base (hex) | Base (dec, origin-1) | Name | Size | Type | C++ name | Enum | Units | Access | Default | Description
147 | Customer Diagnostic Registers - Integer |  | 0001, 0002 | 0 | 1 | DummyReg | 2 | int32_t | DummyReg_i32 | DummyReg_i32 = 1, |  | Read-Only |  | Dummy register; always returns zero; can be used to scan for active MODBUS addresses
1 | Basic Registers - Floating Point | Energy Registers | 1001, 1002 | 3E8 | 1001 | EnergySum | 2 | float | EnergySum_f32 | EnergySum_f32 = 1001, | kWh | Read/Write |  | Total net (bidirectional) energy
2 | Basic Registers - Floating Point | Energy Registers | 1003, 1004 | 3EA | 1003 | EnergyPosSum | 2 | float | EnergyPosSum_f32 | EnergyPosSum_f32 = 1003, | kWh | Read/Write |  | Total positive energy
3 | Basic Registers - Floating Point | Energy Registers | 1005, 1006 | 3EC | 1005 | EnergySumNR | 2 | float | EnergySumNR_f32 | EnergySumNR_f32 = 1005, | kWh | Read-Only |  | Total net (bidirectional) energy - non resettable
4 | Basic Registers - Floating Point | Energy Registers | 1007, 1008 | 3EE | 1007 | EnergyPosSumNR | 2 | float | EnergyPosSumNR_f32 | EnergyPosSumNR_f32 = 1007, | kWh | Read-Only |  | Total positive energy - non resettable
5 | Basic Registers - Floating Point | Power Registers | 1009, 1010 | 3F0 | 1009 | PowerSum | 2 | float | PowerSum_f32 | PowerSum_f32 = 1009, | W | Read-Only |  | Real power, sum of active phases
6 | Basic Registers - Floating Point | Power Registers | 1011, 1012 | 3F2 | 1011 | PowerA | 2 | float | PowerA_f32 | PowerA_f32 = 1011, | W | Read-Only |  | Real power, phase A
7 | Basic Registers - Floating Point | Power Registers | 1013, 1014 | 3F4 | 1013 | PowerB | 2 | float | PowerB_f32 | PowerB_f32 = 1013, | W | Read-Only |  | Real power, phase B
8 | Basic Registers - Floating Point | Power Registers | 1015, 1016 | 3F6 | 1015 | PowerC | 2 | float | PowerC_f32 | PowerC_f32 = 1015, | W | Read-Only |  | Real power, phase C
9 | Basic Registers - Floating Point | Voltage Registers | 1017, 1018 | 3F8 | 1017 | VoltAvgLN | 2 | float | VoltAvgLN_f32 | VoltAvgLN_f32 = 1017, | V | Read-Only |  | Average phase-to-neutral voltage
10 | Basic Registers - Floating Point | Voltage Registers | 1019, 1020 | 3FA | 1019 | VoltA | 2 | float | VoltA_f32 | VoltA_f32 = 1019, | V | Read-Only |  | RMS voltage, phase A to neutral
11 | Basic Registers - Floating Point | Voltage Registers | 1021, 1022 | 3FC | 1021 | VoltB | 2 | float | VoltB_f32 | VoltB_f32 = 1021, | V | Read-Only |  | RMS voltage, phase B to neutral
12 | Basic Registers - Floating Point | Voltage Registers | 1023, 1024 | 3FE | 1023 | VoltC | 2 | float | VoltC_f32 | VoltC_f32 = 1023, | V | Read-Only |  | RMS voltage, phase C to neutral
13 | Basic Registers - Floating Point | Voltage Registers | 1025, 1026 | 400 | 1025 | VoltAvgLL | 2 | float | VoltAvgLL_f32 | VoltAvgLL_f32 = 1025, | V | Read-Only |  | Average line-to-line voltage
14 | Basic Registers - Floating Point | Voltage Registers | 1027, 1028 | 402 | 1027 | VoltAB | 2 | float | VoltAB_f32 | VoltAB_f32 = 1027, | V | Read-Only |  | RMS voltage, line-to-line, phase A to B
15 | Basic Registers - Floating Point | Voltage Registers | 1029, 1030 | 404 | 1029 | VoltBC | 2 | float | VoltBC_f32 | VoltBC_f32 = 1029, | V | Read-Only |  | RMS voltage, line-to-line, phase B to C
16 | Basic Registers - Floating Point | Voltage Registers | 1031, 1032 | 406 | 1031 | VoltAC | 2 | float | VoltAC_f32 | VoltAC_f32 = 1031, | V | Read-Only |  | RMS voltage, line-to-line, phase A to C
17 | Basic Registers - Floating Point | Frequency Register | 1033, 1034 | 408 | 1033 | Freq | 2 | float | Freq_f32 | Freq_f32 = 1033, | Hz | Read-Only |  | Power line frequency
35 | Advanced Registers - Floating Point | Energy Registers | 1101, 1102 | 44C | 1101 | EnergyA | 2 | float | EnergyA_f32 | EnergyA_f32 = 1101, | kWh | Read/Write |  | Net (bidirectional) energy, phase A
36 | Advanced Registers - Floating Point | Energy Registers | 1103, 1104 | 44E | 1103 | EnerygB | 2 | float | EnerygB_f32 | EnerygB_f32 = 1103, | kWh | Read/Write |  | Net (bidirectional) energy, phase B
37 | Advanced Registers - Floating Point | Energy Registers | 1105, 1106 | 450 | 1105 | EnergyC | 2 | float | EnergyC_f32 | EnergyC_f32 = 1105, | kWh | Read/Write |  | Net (bidirectional) energy, phase C
38 | Advanced Registers - Floating Point | Energy Registers | 1107, 1108 | 452 | 1107 | EnergyPosA | 2 | float | EnergyPosA_f32 | EnergyPosA_f32 = 1107, | kWh | Read/Write |  | Positive energy, phase A
39 | Advanced Registers - Floating Point | Energy Registers | 1109, 1110 | 454 | 1109 | EnergyPosB | 2 | float | EnergyPosB_f32 | EnergyPosB_f32 = 1109, | kWh | Read/Write |  | Positive energy, phase B
40 | Advanced Registers - Floating Point | Energy Registers | 1111, 1112 | 456 | 1111 | EnergyPosC | 2 | float | EnergyPosC_f32 | EnergyPosC_f32 = 1111, | kWh | Read/Write |  | Positive energy, phase C
41 | Advanced Registers - Floating Point | Energy Registers | 1113, 1114 | 458 | 1113 | EnergyNegSum | 2 | float | EnergyNegSum_f32 | EnergyNegSum_f32 = 1113, | kWh | Read/Write |  | Negative energy, sum of active phases
42 | Advanced Registers - Floating Point | Energy Registers | 1115, 1116 | 45A | 1115 | EnergyNegSumNR | 2 | float | EnergyNegSumNR_f32 | EnergyNegSumNR_f32 = 1115, | kWh | Read-Only |  | Negative energy, sum of active phases - non resettable
43 | Advanced Registers - Floating Point | Energy Registers | 1117, 1118 | 45C | 1117 | EnergyNegA | 2 | float | EnergyNegA_f32 | EnergyNegA_f32 = 1117, | kWh | Read/Write |  | Negative energy, phase A
44 | Advanced Registers - Floating Point | Energy Registers | 1119, 1120 | 45E | 1119 | EnergyNegB | 2 | float | EnergyNegB_f32 | EnergyNegB_f32 = 1119, | kWh | Read/Write |  | Negative energy, phase B
45 | Advanced Registers - Floating Point | Energy Registers | 1121, 1122 | 460 | 1121 | EnergyNegC | 2 | float | EnergyNegC_f32 | EnergyNegC_f32 = 1121, | kWh | Read/Write |  | Negative energy, phase C
46 | Advanced Registers - Floating Point | Energy Registers | 1123, 1124 | 462 | 1123 | EnergyReacSum | 2 | float | EnergyReacSum_f32 | EnergyReacSum_f32 = 1123, | kVARh | Read/Write |  | Reactive energy, sum of active phases
47 | Advanced Registers - Floating Point | Energy Registers | 1125, 1126 | 464 | 1125 | EnergyReacA | 2 | float | EnergyReacA_f32 | EnergyReacA_f32 = 1125, | kVARh | Read/Write |  | Net reactive energy, phase A
48 | Advanced Registers - Floating Point | Energy Registers | 1127, 1128 | 466 | 1127 | EnergyReacB | 2 | float | EnergyReacB_f32 | EnergyReacB_f32 = 1127, | kVARh | Read/Write |  | Net reactive energy, phase B
49 | Advanced Registers - Floating Point | Energy Registers | 1129, 1130 | 468 | 1129 | EnergyReacC | 2 | float | EnergyReacC_f32 | EnergyReacC_f32 = 1129, | kVARh | Read/Write |  | Net reactive energy, phase C
50 | Advanced Registers - Floating Point | Energy Registers | 1131, 1132 | 46A | 1131 | EnergyAppSum | 2 | float | EnergyAppSum_f32 | EnergyAppSum_f32 = 1131, | kVAh | Read/Write |  | Apparent energy, sum of active phases
51 | Advanced Registers - Floating Point | Energy Registers | 1133, 1134 | 46C | 1133 | EnergyAppA | 2 | float | EnergyAppA_f32 | EnergyAppA_f32 = 1133, | kVAh | Read/Write |  | Apparent energy, phase A
52 | Advanced Registers - Floating Point | Energy Registers | 1135, 1136 | 46E | 1135 | EnergyAppB | 2 | float | EnergyAppB_f32 | EnergyAppB_f32 = 1135, | kVAh | Read/Write |  | Apparent energy, phase B
53 | Advanced Registers - Floating Point | Energy Registers | 1137, 1138 | 470 | 1137 | EnergyAppC | 2 | float | EnergyAppC_f32 | EnergyAppC_f32 = 1137, | kVAh | Read/Write |  | Apparent energy, phase C
54 | Advanced Registers - Floating Point | Power Factor Registers | 1139, 1140 | 472 | 1139 | PowerFactorAvg | 2 | float | PowerFactorAvg_f32 | PowerFactorAvg_f32 = 1139, |  | Read-Only |  | Power factor, average of active phases
55 | Advanced Registers - Floating Point | Power Factor Registers | 1141, 1142 | 474 | 1141 | PowerFactorA | 2 | float | PowerFactorA_f32 | PowerFactorA_f32 = 1141, |  | Read-Only |  | Power factor, phase A
56 | Advanced Registers - Floating Point | Power Factor Registers | 1143, 1144 | 476 | 1143 | PowerFactorB | 2 | float | PowerFactorB_f32 | PowerFactorB_f32 = 1143, |  | Read-Only |  | Power factor, phase B
57 | Advanced Registers - Floating Point | Power Factor Registers | 1145, 1146 | 478 | 1145 | PowerFactorC | 2 | float | PowerFactorC_f32 | PowerFactorC_f32 = 1145, |  | Read-Only |  | Power factor, phase C
58 | Advanced Registers - Floating Point | Reactive and Apparent Power Registers | 1147, 1148 | 47A | 1147 | PowerReacSum | 2 | float | PowerReacSum_f32 | PowerReacSum_f32 = 1147, | VAR | Read-Only |  | Reactive power, sum of active phases
59 | Advanced Registers - Floating Point | Reactive and Apparent Power Registers | 1149, 1150 | 47C | 1149 | PowerReacA | 2 | float | PowerReacA_f32 | PowerReacA_f32 = 1149, | VAR | Read-Only |  | Reactive power, phase A
60 | Advanced Registers - Floating Point | Reactive and Apparent Power Registers | 1151, 1152 | 47E | 1151 | PowerReacB | 2 | float | PowerReacB_f32 | PowerReacB_f32 = 1151, | VAR | Read-Only |  | Reactive power, phase B
61 | Advanced Registers - Floating Point | Reactive and Apparent Power Registers | 1153, 1154 | 480 | 1153 | PowerReacC | 2 | float | PowerReacC_f32 | PowerReacC_f32 = 1153, | VAR | Read-Only |  | Reactive power, phase C
62 | Advanced Registers - Floating Point | Reactive and Apparent Power Registers | 1155, 1156 | 482 | 1155 | PowerAppSum | 2 | float | PowerAppSum_f32 | PowerAppSum_f32 = 1155, | VA | Read-Only |  | Apparent power, sum of active phases
63 | Advanced Registers - Floating Point | Reactive and Apparent Power Registers | 1157, 1158 | 484 | 1157 | PowerAppA | 2 | float | PowerAppA_f32 | PowerAppA_f32 = 1157, | VA | Read-Only |  | Apparent power, phase A
64 | Advanced Registers - Floating Point | Reactive and Apparent Power Registers | 1159, 1160 | 486 | 1159 | PowerAppB | 2 | float | PowerAppB_f32 | PowerAppB_f32 = 1159, | VA | Read-Only |  | Apparent power, phase B
65 | Advanced Registers - Floating Point | Reactive and Apparent Power Registers | 1161, 1162 | 488 | 1161 | PowerAppC | 2 | float | PowerAppC_f32 | PowerAppC_f32 = 1161, | VA | Read-Only |  | Apparent power, phase C
66 | Advanced Registers - Floating Point | Current Registers | 1163, 1164 | 48A | 1163 | CurrentA | 2 | float | CurrentA_f32 | CurrentA_f32 = 1163, | A | Read-Only |  | RMS current, phase A
67 | Advanced Registers - Floating Point | Current Registers | 1165, 1166 | 48C | 1165 | CurrentB | 2 | float | CurrentB_f32 | CurrentB_f32 = 1165, | A | Read-Only |  | RMS current, phase B
68 | Advanced Registers - Floating Point | Current Registers | 1167, 1168 | 48E | 1167 | CurrentC | 2 | float | CurrentC_f32 | CurrentC_f32 = 1167, | A | Read-Only |  | RMS current, phase C
69 | Advanced Registers - Floating Point | Demand Registers | 1169, 1170 | 490 | 1169 | Demand | 2 | float | Demand_f32 | Demand_f32 = 1169, | W | Read-Only |  | Real power demand averaged over the demand period
70 | Advanced Registers - Floating Point | Demand Registers | 1171, 1172 | 492 | 1171 | DemandMin | 2 | float | DemandMin_f32 | DemandMin_f32 = 1171, | W | Read-Only |  | Minimum power demand
71 | Advanced Registers - Floating Point | Demand Registers | 1173, 1174 | 494 | 1173 | DemandMax | 2 | float | DemandMax_f32 | DemandMax_f32 = 1173, | W | Read-Only |  | Maximum power demand
72 | Advanced Registers - Floating Point | Demand Registers | 1175, 1176 | 496 | 1175 | DemandApp | 2 | float | DemandApp_f32 | DemandApp_f32 = 1175, | W | Read-Only |  | Apparent power demand
73 | Advanced Registers - Floating Point | Demand Registers | 1177, 1178 | 498 | 1177 | DemandA | 2 | float | DemandA_f32 | DemandA_f32 = 1177, | W | Read-Only |  | Real power demand, phase A
74 | Advanced Registers - Floating Point | Demand Registers | 1179, 1180 | 49A | 1179 | DemandB | 2 | float | DemandB_f32 | DemandB_f32 = 1179, | W | Read-Only |  | Real power demand, phase B
75 | Advanced Registers - Floating Point | Demand Registers | 1181, 1182 | 49C | 1181 | DemandC | 2 | float | DemandC_f32 | DemandC_f32 = 1181, | W | Read-Only |  | Real power demand, phase C
18 | Basic Registers - Integer | Energy Registers | 1201, 1202 | 4B0 | 1201 | EnergySum | 2 | int32_t | EnergySum_i32 | EnergySum_i32 = 1201, | 0.1 kWh | Read/Write |  | Total net (bidirectional) energy
19 | Basic Registers - Integer | Energy Registers | 1203, 1204 | 4B2 | 1203 | EnergyPosSum | 2 | int32_t | EnergyPosSum_i32 | EnergyPosSum_i32 = 1203, | 0.1 kWh | Read/Write |  | Total positive energy
20 | Basic Registers - Integer | Energy Registers | 1205, 1206 | 4B4 | 1205 | EnergySumNR | 2 | int32_t | EnergySumNR_i32 | EnergySumNR_i32 = 1205, | 0.1 kWh | Read-Only |  | Total net (bidirectional) energy - non resettable
21 | Basic Registers - Integer | Energy Registers | 1207, 1208 | 4B6 | 1207 | EnergyPosSumNR | 2 | int32_t | EnergyPosSumNR_i32 | EnergyPosSumNR_i32 = 1207, | 0.1 kWh | Read-Only |  | Total positive energy - non resettable
22 | Basic Registers - Integer | Power Registers | 1209 | 4B8 | 1209 | PowerSum | 1 | int16_t | PowerSum_i16 | PowerSum_i16 = 1209, | PowerIntScale | Read-Only |  | Real power, sum of active phases
23 | Basic Registers - Integer | Power Registers | 1210 | 4B9 | 1210 | PowerA | 1 | int16_t | PowerA_i16 | PowerA_i16 /* = 1210 */, | PowerIntScale | Read-Only |  | Real power, phase A
24 | Basic Registers - Integer | Power Registers | 1211 | 4BA | 1211 | PowerB | 1 | int16_t | PowerB_i16 | PowerB_i16 /* = 1211 */, | PowerIntScale | Read-Only |  | Real power, phase B
25 | Basic Registers - Integer | Power Registers | 1212 | 4BB | 1212 | PowerC | 1 | int16_t | PowerC_i16 | PowerC_i16 /* = 1212 */, | PowerIntScale | Read-Only |  | Real power, phase C
26 | Basic Registers - Integer | Voltage Registers | 1213 | 4BC | 1213 | VoltAvgLN | 1 | int16_t | VoltAvgLN_i16 | VoltAvgLN_i16 /* = 1213 */, | 0.1 V | Read-Only |  | Average phase-to-neutral voltage
27 | Basic Registers - Integer | Voltage Registers | 1214 | 4BD | 1214 | VoltA | 1 | int16_t | VoltA_i16 | VoltA_i16 /* = 1214 */, | 0.1 V | Read-Only |  | RMS voltage, phase A to neutral
28 | Basic Registers - Integer | Voltage Registers | 1215 | 4BE | 1215 | VoltB | 1 | int16_t | VoltB_i16 | VoltB_i16 /* = 1215 */, | 0.1 V | Read-Only |  | RMS voltage, phase B to neutral
29 | Basic Registers - Integer | Voltage Registers | 1216 | 4BF | 1216 | VoltC | 1 | int16_t | VoltC_i16 | VoltC_i16 /* = 1216 */, | 0.1 V | Read-Only |  | RMS voltage, phase C to neutral
30 | Basic Registers - Integer | Voltage Registers | 1217 | 4C0 | 1217 | VoltAvgLL | 1 | int16_t | VoltAvgLL_i16 | VoltAvgLL_i16 /* = 1217 */, | 0.1 V | Read-Only |  | Average line-to-line voltage
31 | Basic Registers - Integer | Voltage Registers | 1218 | 4C1 | 1218 | VoltAB | 1 | int16_t | VoltAB_i16 | VoltAB_i16 /* = 1218 */, | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase A to B
32 | Basic Registers - Integer | Voltage Registers | 1219 | 4C2 | 1219 | VoltBC | 1 | int16_t | VoltBC_i16 | VoltBC_i16 /* = 1219 */, | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase B to C
33 | Basic Registers - Integer | Voltage Registers | 1220 | 4C3 | 1220 | VoltAC | 1 | int16_t | VoltAC_i16 | VoltAC_i16 /* = 1220 */, | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase A to C
34 | Basic Registers - Integer | Frequency Register | 1221 | 4C4 | 1221 | Freq | 1 | int16_t | Freq_i16 | Freq_i16 /* = 1221 */, | 0.1 Hz | Read-Only |  | Power line frequency
76 | Advanced Registers - Integer | Energy Registers | 1301, 1302 | 514 | 1301 | EnergyA | 2 | int32_t | EnergyA_i32 | EnergyA_i32 = 1301, | 0.1 kWh | Read/Write |  | Net energy, phase A
77 | Advanced Registers - Integer | Energy Registers | 1303, 1304 | 516 | 1303 | EnerygB | 2 | int32_t | EnerygB_i32 | EnerygB_i32 = 1303, | 0.1 kWh | Read/Write |  | Net energy, phase B
78 | Advanced Registers - Integer | Energy Registers | 1305, 1306 | 518 | 1305 | EnergyC | 2 | int32_t | EnergyC_i32 | EnergyC_i32 = 1305, | 0.1 kWh | Read/Write |  | Net energy, phase C
79 | Advanced Registers - Integer | Energy Registers | 1307, 1308 | 51A | 1307 | EnergyPosA | 2 | int32_t | EnergyPosA_i32 | EnergyPosA_i32 = 1307, | 0.1 kWh | Read/Write |  | Positive energy, phase A
80 | Advanced Registers - Integer | Energy Registers | 1309, 1310 | 51C | 1309 | EnergyPosB | 2 | int32_t | EnergyPosB_i32 | EnergyPosB_i32 = 1309, | 0.1 kWh | Read/Write |  | Positive energy, phase B
81 | Advanced Registers - Integer | Energy Registers | 1311, 1312 | 51E | 1311 | EnergyPosC | 2 | int32_t | EnergyPosC_i32 | EnergyPosC_i32 = 1311, | 0.1 kWh | Read/Write |  | Positive energy, phase C
82 | Advanced Registers - Integer | Energy Registers | 1313, 1314 | 520 | 1313 | EnergyNegSum | 2 | int32_t | EnergyNegSum_i32 | EnergyNegSum_i32 = 1313, | 0.1 kWh | Read/Write |  | Negative energy, sum of active phases
83 | Advanced Registers - Integer | Energy Registers | 1315, 1316 | 522 | 1315 | EnergyNegSumNR | 2 | int32_t | EnergyNegSumNR_i32 | EnergyNegSumNR_i32 = 1315, | 0.1 kWh | Read-Only |  | Negative energy, sum of active phases - non resettable
84 | Advanced Registers - Integer | Energy Registers | 1317, 1318 | 524 | 1317 | EnergyNegA | 2 | int32_t | EnergyNegA_i32 | EnergyNegA_i32 = 1317, | 0.1 kWh | Read/Write |  | Negative energy, phase A
85 | Advanced Registers - Integer | Energy Registers | 1319, 1320 | 526 | 1319 | EnergyNegB | 2 | int32_t | EnergyNegB_i32 | EnergyNegB_i32 = 1319, | 0.1 kWh | Read/Write |  | Negative energy, phase B
86 | Advanced Registers - Integer | Energy Registers | 1321, 1322 | 528 | 1321 | EnergyNegC | 2 | int32_t | EnergyNegC_i32 | EnergyNegC_i32 = 1321, | 0.1 kWh | Read/Write |  | Negative energy, phase C
87 | Advanced Registers - Integer | Energy Registers | 1323, 1324 | 52A | 1323 | EnergyReacSum | 2 | int32_t | EnergyReacSum_i32 | EnergyReacSum_i32 = 1323, | 0.1 kVARh | Read/Write |  | Reactive energy, sum of active phases
88 | Advanced Registers - Integer | Energy Registers | 1325, 1326 | 52C | 1325 | EnergyReacA | 2 | int32_t | EnergyReacA_i32 | EnergyReacA_i32 = 1325, | 0.1 kVARh | Read/Write |  | Net reactive energy, phase A
89 | Advanced Registers - Integer | Energy Registers | 1327, 1328 | 52E | 1327 | EnergyReacB | 2 | int32_t | EnergyReacB_i32 | EnergyReacB_i32 = 1327, | 0.1 kVARh | Read/Write |  | Net reactive energy, phase B
90 | Advanced Registers - Integer | Energy Registers | 1329, 1330 | 530 | 1329 | EnergyReacC | 2 | int32_t | EnergyReacC_i32 | EnergyReacC_i32 = 1329, | 0.1 kVARh | Read/Write |  | Net reactive energy, phase C
91 | Advanced Registers - Integer | Energy Registers | 1331, 1332 | 532 | 1331 | EnergyAppSum | 2 | int32_t | EnergyAppSum_i32 | EnergyAppSum_i32 = 1331, | 0.1 kVAh | Read/Write |  | Apparent energy, sum of active phases
92 | Advanced Registers - Integer | Energy Registers | 1333, 1334 | 534 | 1333 | EnergyAppA | 2 | int32_t | EnergyAppA_i32 | EnergyAppA_i32 = 1333, | 0.1 kVAh | Read/Write |  | Apparent energy, phase A
93 | Advanced Registers - Integer | Energy Registers | 1335, 1336 | 536 | 1335 | EnergyAppB | 2 | int32_t | EnergyAppB_i32 | EnergyAppB_i32 = 1335, | 0.1 kVAh | Read/Write |  | Apparent energy, phase B
94 | Advanced Registers - Integer | Energy Registers | 1337, 1338 | 538 | 1337 | EnergyAppC | 2 | int32_t | EnergyAppC_i32 | EnergyAppC_i32 = 1337, | 0.1 kVAh | Read/Write |  | Apparent energy, phase C
95 | Advanced Registers - Integer | Power Factor Registers | 1339 | 53A | 1339 | PowerFactorAvg | 1 | int16_t | PowerFactorAvg_i16 | PowerFactorAvg_i16 = 1339, | 0.01 | Read-Only |  | Power factor, average of active phases
96 | Advanced Registers - Integer | Power Factor Registers | 1340 | 53B | 1340 | PowerFactorA | 1 | int16_t | PowerFactorA_i16 | PowerFactorA_i16 /* = 1340 */, | 0.01 | Read-Only |  | Power factor, phase A
97 | Advanced Registers - Integer | Power Factor Registers | 1341 | 53C | 1341 | PowerFactorB | 1 | int16_t | PowerFactorB_i16 | PowerFactorB_i16 /* = 1341 */, | 0.01 | Read-Only |  | Power factor, phase B
98 | Advanced Registers - Integer | Power Factor Registers | 1342 | 53D | 1342 | PowerFactorC | 1 | int16_t | PowerFactorC_i16 | PowerFactorC_i16 /* = 1342 */, | 0.01 | Read-Only |  | Power factor, phase C
99 | Advanced Registers - Integer | Reactive and Apparent Power Registers | 1343 | 53E | 1343 | PowerReacSum | 1 | int16_t | PowerReacSum_i16 | PowerReacSum_i16 /* = 1343 */, | PowerIntScale | Read-Only |  | Reactive power VAR, sum of active phases
100 | Advanced Registers - Integer | Reactive and Apparent Power Registers | 1344 | 53F | 1344 | PowerReacA | 1 | int16_t | PowerReacA_i16 | PowerReacA_i16 /* = 1344 */, | PowerIntScale | Read-Only |  | Reactive power VAR, phase A
101 | Advanced Registers - Integer | Reactive and Apparent Power Registers | 1345 | 540 | 1345 | PowerReacB | 1 | int16_t | PowerReacB_i16 | PowerReacB_i16 /* = 1345 */, | PowerIntScale | Read-Only |  | Reactive power VAR, phase B
102 | Advanced Registers - Integer | Reactive and Apparent Power Registers | 1346 | 541 | 1346 | PowerReacC | 1 | int16_t | PowerReacC_i16 | PowerReacC_i16 /* = 1346 */, | PowerIntScale | Read-Only |  | Reactive power VAR, phase C
103 | Advanced Registers - Integer | Reactive and Apparent Power Registers | 1347 | 542 | 1347 | PowerAppSum | 1 | int16_t | PowerAppSum_i16 | PowerAppSum_i16 /* = 1347 */, | PowerIntScale | Read-Only |  | Apparent power VA, sum of active phases
104 | Advanced Registers - Integer | Reactive and Apparent Power Registers | 1348 | 543 | 1348 | PowerAppA | 1 | int16_t | PowerAppA_i16 | PowerAppA_i16 /* = 1348 */, | PowerIntScale | Read-Only |  | Apparent power VA, phase A
105 | Advanced Registers - Integer | Reactive and Apparent Power Registers | 1349 | 544 | 1349 | PowerAppB | 1 | int16_t | PowerAppB_i16 | PowerAppB_i16 /* = 1349 */, | PowerIntScale | Read-Only |  | Apparent power VA, phase B
106 | Advanced Registers - Integer | Reactive and Apparent Power Registers | 1350 | 545 | 1350 | PowerAppC | 1 | int16_t | PowerAppC_i16 | PowerAppC_i16 /* = 1350 */, | PowerIntScale | Read-Only |  | Apparent power VA, phase C
107 | Advanced Registers - Integer | Current Registers | 1351 | 546 | 1351 | CurrentA | 1 | int16_t | CurrentA_i16 | CurrentA_i16 /* = 1351 */, | CurrentIntScale | Read-Only |  | RMS current, phase A
108 | Advanced Registers - Integer | Current Registers | 1352 | 547 | 1352 | CurrentB | 1 | int16_t | CurrentB_i16 | CurrentB_i16 /* = 1352 */, | CurrentIntScale | Read-Only |  | RMS current, phase B
109 | Advanced Registers - Integer | Current Registers | 1353 | 548 | 1353 | CurrentC | 1 | int16_t | CurrentC_i16 | CurrentC_i16 /* = 1353 */, | CurrentIntScale | Read-Only |  | RMS current, phase C
110 | Advanced Registers - Integer | Demand Registers | 1354 | 549 | 1354 | Demand | 1 | int16_t | Demand_i16 | Demand_i16 /* = 1354 */, | PowerIntScale | Read-Only |  | Real power demand averaged over the demand period
111 | Advanced Registers - Integer | Demand Registers | 1355 | 54A | 1355 | DemandMin | 1 | int16_t | DemandMin_i16 | DemandMin_i16 /* = 1355 */, | PowerIntScale | Read-Only |  | Minimum power demand
112 | Advanced Registers - Integer | Demand Registers | 1356 | 54B | 1356 | DemandMax | 1 | int16_t | DemandMax_i16 | DemandMax_i16 /* = 1356 */, | PowerIntScale | Read-Only |  | Maximum power demand
113 | Advanced Registers - Integer | Demand Registers | 1357 | 54C | 1357 | DemandApp | 1 | int16_t | DemandApp_i16 | DemandApp_i16 /* = 1357 */, | PowerIntScale | Read-Only |  | Apparent power demand
114 | Advanced Registers - Integer | Demand Registers | 1358 | 54D | 1358 | DemandA | 1 | int16_t | DemandA_i16 | DemandA_i16 /* = 1358 */, | PowerIntScale | Read-Only |  | Real power demand, phase A
115 | Advanced Registers - Integer | Demand Registers | 1359 | 54E | 1359 | DemandB | 1 | int16_t | DemandB_i16 | DemandB_i16 /* = 1359 */, | PowerIntScale | Read-Only |  | Real power demand, phase B
116 | Advanced Registers - Integer | Demand Registers | 1360 | 54F | 1360 | DemandC | 1 | int16_t | DemandC_i16 | DemandC_i16 /* = 1360 */, | PowerIntScale | Read-Only |  | Real power demand, phase C
117 | Advanced Registers - Integer | IoPin | 1361 | 550 | 1361 | IoPinState | 1 | int16_t | IoPinState_i16 | IoPinState_i16 /* = 1361 */, |  | Read/Write |  | IO pin digital input or output state
118 | Advanced Registers - Integer | IoPin | 1362, 1363 | 551 | 1362 | PulseCount | 2 | int32_t | PulseCount_i32 | PulseCount_i32 /* = 1362 */, |  | Read/Write |  | IO pin pulse count
119 | Configuration Registers - Integer |  | 1601, 1602 | 640 | 1601 | ConfigPasscode | 2 | int32_t | ConfigPasscode_i32 | ConfigPasscode_i32 = 1601, |  | Read/Write | 0 | Optional passcode to prevent unauthorized changes to configuration
120 | Configuration Registers - Integer |  | 1603 | 642 | 1603 | CtAmps | 1 | int16_t | CtAmps_i16 | CtAmps_i16 = 1603, | 1 A | Read/Write | 5 | Current transformer rated current
121 | Configuration Registers - Integer |  | 1604 | 643 | 1604 | CtAmpsA | 1 | int16_t | CtAmpsA_i16 | CtAmpsA_i16 /* = 1604 */, | 1 A | Read/Write | 5 | Optional CT rated current override for phase A
122 | Configuration Registers - Integer |  | 1605 | 644 | 1605 | CtAmpsB | 1 | int16_t | CtAmpsB_i16 | CtAmpsB_i16 /* = 1605 */, | 1 A | Read/Write | 5 | Optional CT rated current override for phase B
123 | Configuration Registers - Integer |  | 1606 | 645 | 1606 | CtAmpsC | 1 | int16_t | CtAmpsC_i16 | CtAmpsC_i16 /* = 1606 */, | 1 A | Read/Write | 5 | Optional CT rated current override for phase C
124 | Configuration Registers - Integer |  | 1607 | 646 | 1607 | CtDirections | 1 | int16_t | CtDirections_i16 | CtDirections_i16 /* = 1607 */, |  | Read/Write | 0 | Optionally invert CT orientations
125 | Configuration Registers - Integer |  | 1608 | 647 | 1608 | Averaging | 1 | int16_t | Averaging_i16 | Averaging_i16 /* = 1608 */, |  | Read/Write | 1 (fast) | Configure measurement averaging
126 | Configuration Registers - Integer |  | 1609 | 648 | 1609 | PowerIntScale | 1 | int16_t | PowerIntScale_i16 | PowerIntScale_i16 /* = 1609 */, | 1 W | Read/Write | 0 (auto) | Scale factor for integer power registers
127 | Configuration Registers - Integer |  | 1610 | 649 | 1610 | DemPerMins | 1 | int16_t | DemPerMins_i16 | DemPerMins_i16 /* = 1610 */, | 1 minute | Read/Write | 15 | Demand period
128 | Configuration Registers - Integer |  | 1611 | 64A | 1611 | DemSubints | 1 | int16_t | DemSubints_i16 | DemSubints_i16 /* = 1611 */, |  | Read/Write | 1 | Number of demand subintervals
129 | Configuration Registers - Integer |  | 1612 | 64B | 1612 | GainAdjustA | 1 | int16_t | GainAdjustA_i16 | GainAdjustA_i16 /* = 1612 */, | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for phase A
130 | Configuration Registers - Integer |  | 1613 | 64C | 1613 | GainAdjustB | 1 | int16_t | GainAdjustB_i16 | GainAdjustB_i16 /* = 1613 */, | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for phase B
131 | Configuration Registers - Integer |  | 1614 | 64D | 1614 | GainAdjustC | 1 | int16_t | GainAdjustC_i16 | GainAdjustC_i16 /* = 1614 */, | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for phase C
132 | Configuration Registers - Integer |  | 1615 | 64E | 1615 | PhaseAdjustA | 1 | int16_t | PhaseAdjustA_i16 | PhaseAdjustA_i16 /* = 1615 */, | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for phase A
133 | Configuration Registers - Integer |  | 1616 | 64F | 1616 | PhaseAdjustB | 1 | int16_t | PhaseAdjustB_i16 | PhaseAdjustB_i16 /* = 1616 */, | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for phase B
134 | Configuration Registers - Integer |  | 1617 | 650 | 1617 | PhaseAdjustC | 1 | int16_t | PhaseAdjustC_i16 | PhaseAdjustC_i16 /* = 1617 */, | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for phase C
135 | Configuration Registers - Integer |  | 1618 | 651 | 1618 | CreepLimit | 1 | int16_t | CreepLimit_i16 | CreepLimit_i16 /* = 1618 */, |  | Read/Write | 1500 | Configure minimum power for a non-zero reading
136 | Configuration Registers - Integer |  | 1619 | 652 | 1619 | PhaseOffset | 1 | int16_t | PhaseOffset_i16 | PhaseOffset_i16 /* = 1619 */, | 1 degree | Read/Write | 120 | Nominal angle between primary voltage phases (0, 60, 90, 120, or 180)
137 | Configuration Registers - Integer |  | 1620 | 653 | 1620 | ZeroEnergy | 1 | int16_t | ZeroEnergy_i16 | ZeroEnergy_i16 /* = 1620 */, |  | Read/Write | - | Write 1 to zero all resettable energy registers
138 | Configuration Registers - Integer |  | 1621 | 654 | 1621 | ZeroDemand | 1 | int16_t | ZeroDemand_i16 | ZeroDemand_i16 /* = 1621 */, |  | Read/Write | - | Write 1 to zero all demand values
139 | Configuration Registers - Integer |  | 1622 | 655 | 1622 | CurrentIntScale | 1 | int16_t | CurrentIntScale_i16 | CurrentIntScale_i16 /* = 1622 */, |  | Read/Write | 20000 | Scale factor for integer current registers
140 | Configuration Registers - Integer |  | 1623 | 656 | 1623 | IoPinMode | 1 | int16_t | IoPinMode_i16 | IoPinMode_i16 /* = 1623 */, |  | Read/Write | 0 | 0 = IO feature disabled 1 = Falling edge pulse counter and digital input 2 = Rising edge pulse counter and digital input 3 = Open-drain output restores state at power-up 4 = Open-drain output goes low at power-up 5 = Open-drain output goes high at power-up 6 = Push-pull output restores state at power-up 7 = Push-pull output goes low at power-up 8 = Push-pull output goes high at power-up
141 | Communication Registers |  | 1651 | 672 | 1651 | ApplyComConfig | 1 | int16_t | ApplyComConfig_i16 | ApplyComConfig_i16 = 1651, |  | Read/Write | 0 | Writing 1234 applies the configuration settings below. Reads 1 if changes not applied yet.
142 | Communication Registers |  | 1652 | 673 | 1652 | Address | 1 | int16_t | Address_i16 | Address_i16 /* = 1652 */, |  | Read/Write | 0 | MODBUS address (if non-zero, overrides DIP switches)
143 | Communication Registers |  | 1653 | 674 | 1653 | BaudRate | 1 | int16_t | BaudRate_i16 | BaudRate_i16 /* = 1653 */, |  | Read/Write | 0 | 0 = DIP Switch Assigned 4 = 9600 baud 5 = 19200 baud 6 = 38400 baud
144 | Communication Registers |  | 1654 | 675 | 1654 | ParityMode | 1 | int16_t | ParityMode_i16 | ParityMode_i16 /* = 1654 */, |  | Read/Write | 0 | 0 = N81 (no parity, one stop bit) 1 = E81 (even parity, one stop bit)
145 | Communication Registers |  | 1655 | 676 | 1655 | ModbusMode | 1 | int16_t | ModbusMode_i16 | ModbusMode_i16 /* = 1655 */, |  | Read/Write | 0 | 0=RTU 1=TCP-RTU
146 | Communication Registers |  | 1656 | 677 | 1656 | ReplyDelay | 1 | int16_t | ReplyDelay_i16 | ReplyDelay_i16 /* = 1656 */, |  | Read/Write | 5 | Minimum Modbus reply delay. 5 to 180 ms
148 | Customer Diagnostic Registers - Integer |  | 1701, 1702 | 6A4 | 1701 | SerialNumber | 2 | int32_t | SerialNumber_i32 | SerialNumber_i32 = 1701, |  | Read-Only |  | The unique WattNode serial number
149 | Customer Diagnostic Registers - Integer |  | 1703, 1704 | 6A6 | 1703 | UptimeSecs | 2 | int32_t | UptimeSecs_i32 | UptimeSecs_i32 = 1703, | Seconds | Read-Only |  | Time in seconds since last power on
150 | Customer Diagnostic Registers - Integer |  | 1705, 1706 | 6A8 | 1705 | TotalSecs | 2 | int32_t | TotalSecs_i32 | TotalSecs_i32 = 1705, | Seconds | Read-Only |  | Total seconds of operation
151 | Customer Diagnostic Registers - Integer |  | 1707 | 6AA | 1707 | Model | 1 | int16_t | Model_i16 | Model_i16 = 1707, |  | Read-Only |  | Encoded WattNode model
152 | Customer Diagnostic Registers - Integer |  | 1708 | 6AB | 1708 | Version | 1 | int16_t | Version_i16 | Version_i16 /* = 1708 */, |  | Read-Only |  | Firmware version
153 | Customer Diagnostic Registers - Integer |  | 1709 | 6AC | 1709 | Options | 1 | int16_t | Options_i16 | Options_i16 /* = 1709 */, |  | Read-Only |  | WattNode options
154 | Customer Diagnostic Registers - Integer |  | 1710 | 6AD | 1710 | ErrorStatus | 1 | int16_t | ErrorStatus_i16 | ErrorStatus_i16 /* = 1710 */, | n.a. | Read/Write |  | List of recent errors and events
155 | Customer Diagnostic Registers - Integer |  | 1711 | 6AE | 1711 | PowerFailCount | 1 | int16_t | PowerFailCount_i16 | PowerFailCount_i16 /* = 1711 */, |  | Read/Write |  | Power failure count
156 | Customer Diagnostic Registers - Integer |  | 1712 | 6AF | 1712 | CrcErrorCount | 1 | int16_t | CrcErrorCount_i16 | CrcErrorCount_i16 /* = 1712 */, |  | Read/Write |  | Count of MODBUS CRC communication errors
157 | Customer Diagnostic Registers - Integer |  | 1713 | 6B0 | 1713 | FrameErrorCount | 1 | int16_t | FrameErrorCount_i16 | FrameErrorCount_i16 /* = 1713 */, |  | Read/Write |  | Count of MODBUS framing errors
158 | Customer Diagnostic Registers - Integer |  | 1714 | 6B1 | 1714 | PacketErrorCount | 1 | int16_t | PacketErrorCount_i16 | PacketErrorCount_i16 /* = 1714 */, |  | Read/Write |  | Count of bad MODBUS packets
159 | Customer Diagnostic Registers - Integer |  | 1715 | 6B2 | 1715 | OverrunCount | 1 | int16_t | OverrunCount_i16 | OverrunCount_i16 /* = 1715 */, |  | Read/Write |  | Count of MODBUS buffer overruns
160 | Customer Diagnostic Registers - Integer |  | 1716 | 6B3 | 1716 | ErrorStatus1 | 1 | int16_t | ErrorStatus1_i16 | ErrorStatus1_i16 /* = 1716 */, | n.a. | Read/Write |  | Newest error or event (0 = no errors)
161 | Customer Diagnostic Registers - Integer |  | 1717 | 6B4 | 1717 | ErrorStatus2 | 1 | int16_t | ErrorStatus2_i16 | ErrorStatus2_i16 /* = 1717 */, | n.a. | Read/Write |  | Next oldest error or event
162 | Customer Diagnostic Registers - Integer |  | 1718 | 6B5 | 1718 | ErrorStatus3 | 1 | int16_t | ErrorStatus3_i16 | ErrorStatus3_i16 /* = 1718 */, | n.a. | Read/Write |  | Next oldest error or event
163 | Customer Diagnostic Registers - Integer |  | 1719 | 6B6 | 1719 | ErrorStatus4 | 1 | int16_t | ErrorStatus4_i16 | ErrorStatus4_i16 /* = 1719 */, | n.a. | Read/Write |  | Next oldest error or event
164 | Customer Diagnostic Registers - Integer |  | 1720 | 6B7 | 1720 | ErrorStatus5 | 1 | int16_t | ErrorStatus5_i16 | ErrorStatus5_i16 /* = 1720 */, | n.a. | Read/Write |  | Next oldest error or event
165 | Customer Diagnostic Registers - Integer |  | 1721 | 6B8 | 1721 | ErrorStatus6 | 1 | int16_t | ErrorStatus6_i16 | ErrorStatus6_i16 /* = 1721 */, | n.a. | Read/Write |  | Next oldest error or event
166 | Customer Diagnostic Registers - Integer |  | 1722 | 6B9 | 1722 | ErrorStatus7 | 1 | int16_t | ErrorStatus7_i16 | ErrorStatus7_i16 /* = 1722 */, | n.a. | Read/Write |  | Next oldest error or event
167 | Customer Diagnostic Registers - Integer |  | 1723 | 6BA | 1723 | ErrorStatus8 | 1 | int16_t | ErrorStatus8_i16 | ErrorStatus8_i16 /* = 1723 */, | n.a. | Read/Write |  | Oldest error or event
Note on N3: Before version 16, this was Read-Only
Note on N4: Before version 16, this was Read-Only
Note on N20: Before version 16, this was Read-Only
Note on N21: Before version 16, this was Read-Only
Note on N22: Before version 16, this was Read-Only
Note on N23: Before version 16, this was Read-Only
Note on N24: Before version 16, this was Read-Only
Note on N25: Before version 16, this was Read-Only
Note on N26: Before version 16, this was Read-Only
Note on N28: Before version 16, this was Read-Only
Note on N29: Before version 16, this was Read-Only
Note on N30: Before version 16, this was Read-Only
Note on N31: Before version 16, this was Read-Only
Note on N32: Before version 16, this was Read-Only
Note on N33: Before version 16, this was Read-Only
Note on N34: Before version 16, this was Read-Only
Note on N35: Before version 16, this was Read-Only
Note on N36: Before version 16, this was Read-Only
Note on N37: Before version 16, this was Read-Only
Note on N38: Before version 16, this was Read-Only
Note on E58: Register added on version 16
Note on E59: Register added on version 16
Note on E60: Register added on version 16
Note on N61: Before version 16, this was Read-Only
Note on N62: Before version 16, this was Read-Only
Note on N78: Before version 16, this was Read-Only
Note on N79: Before version 16, this was Read-Only
Note on N80: Before version 16, this was Read-Only
Note on N81: Before version 16, this was Read-Only
Note on N82: Before version 16, this was Read-Only
Note on N83: Before version 16, this was Read-Only
Note on N84: Before version 16, this was Read-Only
Note on N86: Before version 16, this was Read-Only
Note on N87: Before version 16, this was Read-Only
Note on N88: Before version 16, this was Read-Only
Note on N89: Before version 16, this was Read-Only
Note on N90: Before version 16, this was Read-Only
Note on N91: Before version 16, this was Read-Only
Note on N92: Before version 16, this was Read-Only
Note on N93: Before version 16, this was Read-Only
Note on N94: Before version 16, this was Read-Only
Note on N95: Before version 16, this was Read-Only
Note on N96: Before version 16, this was Read-Only
Note on E116: Register added on version 16
Note on E117: Register added on version 16
Note on E118: Register added on version 16
Note on E119: Register added on version 16
Note on N119: Can only be written when the IO pin is configured as an output (in modes 3 to 8)
Note on E120: Register added on version 16
Note on N122: On version 16, this assigns the same value to all 3 per-phase CtAmps registers when written. It reads zero unless all three per-phase CtAmps registers are the same, in which case it reads back that value.
Note on O123: Before version 16, this defaulted to zero.
Note on O124: Before version 16, this defaulted to zero.
Note on O125: Before version 16, this defaulted to zero.
Note on P138: Before version 16 only 0, 120 and 180 were allowed.
Note on E141: Register added on version 16
Note on E142: Register added on version 16
Note on E148: Register added on version 16

## Pivot
Count of C++ name
C++ name | Total
Address_i16 | 1
ApplyComConfig_i16 | 1
Averaging_i16 | 1
BaudRate_i16 | 1
ConfigPasscode_i32 | 1
CrcErrorCount_i16 | 1
CreepLimit_i16 | 1
CtAmps_i16 | 1
CtAmpsA_i16 | 1
CtAmpsB_i16 | 1
CtAmpsC_i16 | 1
CtDirections_i16 | 1
CurrentA_f32 | 1
CurrentA_i16 | 1
CurrentB_f32 | 1
CurrentB_i16 | 1
CurrentC_f32 | 1
CurrentC_i16 | 1
CurrentIntScale_i16 | 1
Demand_f32 | 1
Demand_i16 | 1
DemandA_f32 | 1
DemandA_i16 | 1
DemandApp_f32 | 1
DemandApp_i16 | 1
DemandB_f32 | 1
DemandB_i16 | 1
DemandC_f32 | 1
DemandC_i16 | 1
DemandMax_f32 | 1
DemandMax_i16 | 1
DemandMin_f32 | 1
DemandMin_i16 | 1
DemPerMins_i16 | 1
DemSubints_i16 | 1
DummyReg_i32 | 1
EnergyA_f32 | 1
EnergyA_i32 | 1
EnergyAppA_f32 | 1
EnergyAppA_i32 | 1
EnergyAppB_f32 | 1
EnergyAppB_i32 | 1
EnergyAppC_f32 | 1
EnergyAppC_i32 | 1
EnergyAppSum_f32 | 1
EnergyAppSum_i32 | 1
EnergyC_f32 | 1
EnergyC_i32 | 1
EnergyNegA_f32 | 1
EnergyNegA_i32 | 1
EnergyNegB_f32 | 1
EnergyNegB_i32 | 1
EnergyNegC_f32 | 1
EnergyNegC_i32 | 1
EnergyNegSum_f32 | 1
EnergyNegSum_i32 | 1
EnergyNegSumNR_f32 | 1
EnergyNegSumNR_i32 | 1
EnergyPosA_f32 | 1
EnergyPosA_i32 | 1
EnergyPosB_f32 | 1
EnergyPosB_i32 | 1
EnergyPosC_f32 | 1
EnergyPosC_i32 | 1
EnergyPosSum_f32 | 1
EnergyPosSum_i32 | 1
EnergyPosSumNR_f32 | 1
EnergyPosSumNR_i32 | 1
EnergyReacA_f32 | 1
EnergyReacA_i32 | 1
EnergyReacB_f32 | 1
EnergyReacB_i32 | 1
EnergyReacC_f32 | 1
EnergyReacC_i32 | 1
EnergyReacSum_f32 | 1
EnergyReacSum_i32 | 1
EnergySum_f32 | 1
EnergySum_i32 | 1
EnergySumNR_f32 | 1
EnergySumNR_i32 | 1
EnerygB_f32 | 1
EnerygB_i32 | 1
ErrorStatus_i16 | 1
ErrorStatus1_i16 | 1
ErrorStatus2_i16 | 1
ErrorStatus3_i16 | 1
ErrorStatus4_i16 | 1
ErrorStatus5_i16 | 1
ErrorStatus6_i16 | 1
ErrorStatus7_i16 | 1
ErrorStatus8_i16 | 1
FrameErrorCount_i16 | 1
Freq_f32 | 1
Freq_i16 | 1
GainAdjustA_i16 | 1
GainAdjustB_i16 | 1
GainAdjustC_i16 | 1
IoPinMode_i16 | 1
IoPinState_i16 | 1
ModbusMode_i16 | 1
Model_i16 | 1
Options_i16 | 1
OverrunCount_i16 | 1
PacketErrorCount_i16 | 1
ParityMode_i16 | 1
PhaseAdjustA_i16 | 1
PhaseAdjustB_i16 | 1
PhaseAdjustC_i16 | 1
PhaseOffset_i16 | 1
PowerA_f32 | 1
PowerA_i16 | 1
PowerAppA_f32 | 1
PowerAppA_i16 | 1
PowerAppB_f32 | 1
PowerAppB_i16 | 1
PowerAppC_f32 | 1
PowerAppC_i16 | 1
PowerAppSum_f32 | 1
PowerAppSum_i16 | 1
PowerB_f32 | 1
PowerB_i16 | 1
PowerC_f32 | 1
PowerC_i16 | 1
PowerFactorA_f32 | 1
PowerFactorA_i16 | 1
PowerFactorAvg_f32 | 1
PowerFactorAvg_i16 | 1
PowerFactorB_f32 | 1
PowerFactorB_i16 | 1
PowerFactorC_f32 | 1
PowerFactorC_i16 | 1
PowerFailCount_i16 | 1
PowerIntScale_i16 | 1
PowerReacA_f32 | 1
PowerReacA_i16 | 1
PowerReacB_f32 | 1
PowerReacB_i16 | 1
PowerReacC_f32 | 1
PowerReacC_i16 | 1
PowerReacSum_f32 | 1
PowerReacSum_i16 | 1
PowerSum_f32 | 1
PowerSum_i16 | 1
PulseCount_i32 | 1
ReplyDelay_i16 | 1
SerialNumber_i32 | 1
TotalSecs_i32 | 1
UptimeSecs_i32 | 1
Version_i16 | 1
VoltA_f32 | 1
VoltA_i16 | 1
VoltAB_f32 | 1
VoltAB_i16 | 1
VoltAC_f32 | 1
VoltAC_i16 | 1
VoltAvgLL_f32 | 1
VoltAvgLL_i16 | 1
VoltAvgLN_f32 | 1
VoltAvgLN_i16 | 1
VoltB_f32 | 1
VoltB_i16 | 1
VoltBC_f32 | 1
VoltBC_i16 | 1
VoltC_f32 | 1
VoltC_i16 | 1
ZeroDemand_i16 | 1
ZeroEnergy_i16 | 1
Grand Total | 167