## Sheet1
WattNode MODBUS Register List
Firmware Version: 18 |  |  | Date: 2011-11-30 |  |  | Changes since ver. 12 are highlighted green
Basic Registers - Floating Point
| Registers | Name | Units | Access | Default | Description
Energy Registers
| 1001, 1002 | EnergySum | kWh | Read/Write |  | Total net (bidirectional) energy
| 1003, 1004 | EnergyPosSum | kWh | Read/Write |  | Total positive energy
| 1005, 1006 | EnergySumNR | kWh | Read-Only |  | Total net (bidirectional) energy - non resettable
| 1007, 1008 | EnergyPosSumNR | kWh | Read-Only |  | Total positive energy - non resettable
Power Registers
| 1009, 1010 | PowerSum | W | Read-Only |  | Real power, sum of active phases
| 1011, 1012 | PowerA | W | Read-Only |  | Real power, phase A
| 1013, 1014 | PowerB | W | Read-Only |  | Real power, phase B
| 1015, 1016 | PowerC | W | Read-Only |  | Real power, phase C
Voltage Registers
| 1017, 1018 | VoltAvgLN | V | Read-Only |  | Average phase-to-neutral voltage
| 1019, 1020 | VoltA | V | Read-Only |  | RMS voltage, phase A to neutral
| 1021, 1022 | VoltB | V | Read-Only |  | RMS voltage, phase B to neutral
| 1023, 1024 | VoltC | V | Read-Only |  | RMS voltage, phase C to neutral
| 1025, 1026 | VoltAvgLL | V | Read-Only |  | Average line-to-line voltage
| 1027, 1028 | VoltAB | V | Read-Only |  | RMS voltage, line-to-line, phase A to B
| 1029, 1030 | VoltBC | V | Read-Only |  | RMS voltage, line-to-line, phase B to C
| 1031, 1032 | VoltAC | V | Read-Only |  | RMS voltage, line-to-line, phase A to C
Frequency Register
| 1033, 1034 | Freq | Hz | Read-Only |  | Power line frequency
Basic Registers - Integer
| Registers | Name | Units | Access | Default | Description
Energy Registers
| 1201, 1202 | EnergySum | 0.1 kWh | Read/Write |  | Total net (bidirectional) energy
| 1203, 1204 | EnergyPosSum | 0.1 kWh | Read/Write |  | Total positive energy
| 1205, 1206 | EnergySumNR | 0.1 kWh | Read-Only |  | Total net (bidirectional) energy - non resettable
| 1207, 1208 | EnergyPosSumNR | 0.1 kWh | Read-Only |  | Total positive energy - non resettable
Power Registers
| 1209 | PowerSum | PowerIntScale | Read-Only |  | Real power, sum of active phases
| 1210 | PowerA | PowerIntScale | Read-Only |  | Real power, phase A
| 1211 | PowerB | PowerIntScale | Read-Only |  | Real power, phase B
| 1212 | PowerC | PowerIntScale | Read-Only |  | Real power, phase C
Voltage Registers
| 1213 | VoltAvgLN | 0.1 V | Read-Only |  | Average phase-to-neutral voltage
| 1214 | VoltA | 0.1 V | Read-Only |  | RMS voltage, phase A to neutral
| 1215 | VoltB | 0.1 V | Read-Only |  | RMS voltage, phase B to neutral
| 1216 | VoltC | 0.1 V | Read-Only |  | RMS voltage, phase C to neutral
| 1217 | VoltAvgLL | 0.1 V | Read-Only |  | Average line-to-line voltage
| 1218 | VoltAB | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase A to B
| 1219 | VoltBC | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase B to C
| 1220 | VoltAC | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase A to C
Frequency Register
| 1221 | Freq | 0.1 Hz | Read-Only |  | Power line frequency
Advanced Registers - Floating Point
| Registers | Name | Units | Access | Default | Description
Energy Registers
| 1101, 1102 | EnergyA | kWh | Read/Write |  | Net (bidirectional) energy, phase A
| 1103, 1104 | EnerygB | kWh | Read/Write |  | Net (bidirectional) energy, phase B
| 1105, 1106 | EnergyC | kWh | Read/Write |  | Net (bidirectional) energy, phase C
| 1107, 1108 | EnergyPosA | kWh | Read/Write |  | Positive energy, phase A
| 1109, 1110 | EnergyPosB | kWh | Read/Write |  | Positive energy, phase B
| 1111, 1112 | EnergyPosC | kWh | Read/Write |  | Positive energy, phase C
| 1113, 1114 | EnergyNegSum | kWh | Read/Write |  | Negative energy, sum of active phases
| 1115, 1116 | EnergyNegSumNR | kWh | Read-Only |  | Negative energy, sum of active phases - non resettable
| 1117, 1118 | EnergyNegA | kWh | Read/Write |  | Negative energy, phase A
| 1119, 1120 | EnergyNegB | kWh | Read/Write |  | Negative energy, phase B
| 1121, 1122 | EnergyNegC | kWh | Read/Write |  | Negative energy, phase C
| 1123, 1124 | EnergyReacSum | kVARh | Read/Write |  | Reactive energy, sum of active phases
| 1125, 1126 | EnergyReacA | kVARh | Read/Write |  | Net reactive energy, phase A
| 1127, 1128 | EnergyReacB | kVARh | Read/Write |  | Net reactive energy, phase B
| 1129, 1130 | EnergyReacC | kVARh | Read/Write |  | Net reactive energy, phase C
| 1131, 1132 | EnergyAppSum | kVAh | Read/Write |  | Apparent energy, sum of active phases
| 1133, 1134 | EnergyAppA | kVAh | Read/Write |  | Apparent energy, phase A
| 1135, 1136 | EnergyAppB | kVAh | Read/Write |  | Apparent energy, phase B
| 1137, 1138 | EnergyAppC | kVAh | Read/Write |  | Apparent energy, phase C
Power Factor Registers
| 1139, 1140 | PowerFactorAvg |  | Read-Only |  | Power factor, average of active phases
| 1141, 1142 | PowerFactorA |  | Read-Only |  | Power factor, phase A
| 1143, 1144 | PowerFactorB |  | Read-Only |  | Power factor, phase B
| 1145, 1146 | PowerFactorC |  | Read-Only |  | Power factor, phase C
Reactive and Apparent Power Registers
| 1147, 1148 | PowerReacSum | VAR | Read-Only |  | Reactive power, sum of active phases
| 1149, 1150 | PowerReacA | VAR | Read-Only |  | Reactive power, phase A
| 1151, 1152 | PowerReacB | VAR | Read-Only |  | Reactive power, phase B
| 1153, 1154 | PowerReacC | VAR | Read-Only |  | Reactive power, phase C
| 1155, 1156 | PowerAppSum | VA | Read-Only |  | Apparent power, sum of active phases
| 1157, 1158 | PowerAppA | VA | Read-Only |  | Apparent power, phase A
| 1159, 1160 | PowerAppB | VA | Read-Only |  | Apparent power, phase B
| 1161, 1162 | PowerAppC | VA | Read-Only |  | Apparent power, phase C
Current Registers
| 1163, 1164 | CurrentA | A | Read-Only |  | RMS current, phase A
| 1165, 1166 | CurrentB | A | Read-Only |  | RMS current, phase B
| 1167, 1168 | CurrentC | A | Read-Only |  | RMS current, phase C
Demand Registers
| 1169, 1170 | Demand | W | Read-Only |  | Real power demand averaged over the demand period
| 1171, 1172 | DemandMin | W | Read-Only |  | Minimum power demand
| 1173, 1174 | DemandMax | W | Read-Only |  | Maximum power demand
| 1175, 1176 | DemandApp | W | Read-Only |  | Apparent power demand
| 1177, 1178 | DemandA | W | Read-Only |  | Real power demand, phase A
| 1179, 1180 | DemandB | W | Read-Only |  | Real power demand, phase B
| 1181, 1182 | DemandC | W | Read-Only |  | Real power demand, phase C
Advanced Registers - Integer
| Registers | Name | Units | Access | Default | Description
Energy Registers
| 1301, 1302 | EnergyA | 0.1 kWh | Read/Write |  | Net energy, phase A
| 1303, 1304 | EnerygB | 0.1 kWh | Read/Write |  | Net energy, phase B
| 1305, 1306 | EnergyC | 0.1 kWh | Read/Write |  | Net energy, phase C
| 1307, 1308 | EnergyPosA | 0.1 kWh | Read/Write |  | Positive energy, phase A
| 1309, 1310 | EnergyPosB | 0.1 kWh | Read/Write |  | Positive energy, phase B
| 1311, 1312 | EnergyPosC | 0.1 kWh | Read/Write |  | Positive energy, phase C
| 1313, 1314 | EnergyNegSum | 0.1 kWh | Read/Write |  | Negative energy, sum of active phases
| 1315, 1316 | EnergyNegSumNR | 0.1 kWh | Read-Only |  | Negative energy, sum of active phases - non resettable
| 1317, 1318 | EnergyNegA | 0.1 kWh | Read/Write |  | Negative energy, phase A
| 1319, 1320 | EnergyNegB | 0.1 kWh | Read/Write |  | Negative energy, phase B
| 1321, 1322 | EnergyNegC | 0.1 kWh | Read/Write |  | Negative energy, phase C
| 1323, 1324 | EnergyReacSum | 0.1 kVARh | Read/Write |  | Reactive energy, sum of active phases
| 1325, 1326 | EnergyReacA | 0.1 kVARh | Read/Write |  | Net reactive energy, phase A
| 1327, 1328 | EnergyReacB | 0.1 kVARh | Read/Write |  | Net reactive energy, phase B
| 1329, 1330 | EnergyReacC | 0.1 kVARh | Read/Write |  | Net reactive energy, phase C
| 1331, 1332 | EnergyAppSum | 0.1 kVAh | Read/Write |  | Apparent energy, sum of active phases
| 1333, 1334 | EnergyAppA | 0.1 kVAh | Read/Write |  | Apparent energy, phase A
| 1335, 1336 | EnergyAppB | 0.1 kVAh | Read/Write |  | Apparent energy, phase B
| 1337, 1338 | EnergyAppC | 0.1 kVAh | Read/Write |  | Apparent energy, phase C
Power Factor Registers
| 1339 | PowerFactorAvg | 0.01 | Read-Only |  | Power factor, average of active phases
| 1340 | PowerFactorA | 0.01 | Read-Only |  | Power factor, phase A
| 1341 | PowerFactorB | 0.01 | Read-Only |  | Power factor, phase B
| 1342 | PowerFactorC | 0.01 | Read-Only |  | Power factor, phase C
Reactive and Apparent Power Registers
| 1343 | PowerReacSum | PowerIntScale | Read-Only |  | Reactive power VAR, sum of active phases
| 1344 | PowerReacA | PowerIntScale | Read-Only |  | Reactive power VAR, phase A
| 1345 | PowerReacB | PowerIntScale | Read-Only |  | Reactive power VAR, phase B
| 1346 | PowerReacC | PowerIntScale | Read-Only |  | Reactive power VAR, phase C
| 1347 | PowerAppSum | PowerIntScale | Read-Only |  | Apparent power VA, sum of active phases
| 1348 | PowerAppA | PowerIntScale | Read-Only |  | Apparent power VA, phase A
| 1349 | PowerAppB | PowerIntScale | Read-Only |  | Apparent power VA, phase B
| 1350 | PowerAppC | PowerIntScale | Read-Only |  | Apparent power VA, phase C
Current Registers
| 1351 | CurrentA | CurrentIntScale | Read-Only |  | RMS current, phase A
| 1352 | CurrentB | CurrentIntScale | Read-Only |  | RMS current, phase B
| 1353 | CurrentC | CurrentIntScale | Read-Only |  | RMS current, phase C
Demand Registers
| 1354 | Demand | PowerIntScale | Read-Only |  | Real power demand averaged over the demand period
| 1355 | DemandMin | PowerIntScale | Read-Only |  | Minimum power demand
| 1356 | DemandMax | PowerIntScale | Read-Only |  | Maximum power demand
| 1357 | DemandApp | PowerIntScale | Read-Only |  | Apparent power demand
| 1358 | DemandA | PowerIntScale | Read-Only |  | Real power demand, phase A
| 1359 | DemandB | PowerIntScale | Read-Only |  | Real power demand, phase B
| 1360 | DemandC | PowerIntScale | Read-Only |  | Real power demand, phase C
| 1361 | IoPinState |  | Read/Write |  | IO pin digital input or output state
| 1362, 1363 | PulseCount |  | Read/Write |  | IO pin pulse count
Configuration Registers - Integer
| Registers | Name | Units | Access | Default | Description
| 1601, 1602 | ConfigPasscode |  | Read/Write | 0 | Optional passcode to prevent unauthorized changes to configuration
| 1603 | CtAmps | 1 A | Read/Write | 5 | Current transformer rated current
| 1604 | CtAmpsA | 1 A | Read/Write | 5 | Optional CT rated current override for phase A
| 1605 | CtAmpsB | 1 A | Read/Write | 5 | Optional CT rated current override for phase B
| 1606 | CtAmpsC | 1 A | Read/Write | 5 | Optional CT rated current override for phase C
| 1607 | CtDirections |  | Read/Write | 0 | Optionally invert CT orientations
| 1608 | Averaging |  | Read/Write | 1 (fast) | Configure measurement averaging
| 1609 | PowerIntScale | 1 W | Read/Write | 0 (auto) | Scale factor for integer power registers
| 1610 | DemPerMins | 1 minute | Read/Write | 15 | Demand period
| 1611 | DemSubints |  | Read/Write | 1 | Number of demand subintervals
| 1612 | GainAdjustA | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for phase A
| 1613 | GainAdjustB | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for phase B
| 1614 | GainAdjustC | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for phase C
| 1615 | PhaseAdjustA | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for phase A
| 1616 | PhaseAdjustB | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for phase B
| 1617 | PhaseAdjustC | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for phase C
| 1618 | CreepLimit |  | Read/Write | 1500 | Configure minimum power for a non-zero reading
| 1619 | PhaseOffset | 1 degree | Read/Write | 120 | Nominal angle between primary voltage phases (0, 60, 90, 120, or 180)
| 1620 | ZeroEnergy |  | Read/Write | - | Write 1 to zero all resettable energy registers
| 1621 | ZeroDemand |  | Read/Write | - | Write 1 to zero all demand values
| 1622 | CurrentIntScale |  | Read/Write | 20000 | Scale factor for integer current registers
| 1623 | IoPinMode |  | Read/Write | 0 | 0 = IO feature disabled 1 = Falling edge pulse counter and digital input 2 = Rising edge pulse counter and digital input 3 = Open-drain output restores state at power-up 4 = Open-drain output goes low at power-up 5 = Open-drain output goes high at power-up 6 = Push-pull output restores state at power-up 7 = Push-pull output goes low at power-up 8 = Push-pull output goes high at power-up
Communication Registers
| Registers | Name | Units | Access | Default | Description
| 1651 | ApplyComConfig |  | Read/Write | 0 | Writing 1234 applies the configuration settings below. Reads 1 if changes not applied yet.
| 1652 | Address |  | Read/Write | 0 | MODBUS address (if non-zero, overrides DIP switches)
| 1653 | BaudRate |  | Read/Write | 0 | 0 = DIP Switch Assigned 4 = 9600 baud 5 = 19200 baud 6 = 38400 baud
| 1654 | ParityMode |  | Read/Write | 0 | 0 = N81 (no parity, one stop bit) 1 = E81 (even parity, one stop bit)
| 1655 | ModbusMode |  | Read/Write | 0 | 0=RTU 1=TCP-RTU
| 1656 | ReplyDelay |  | Read/Write | 5 | Minimum Modbus reply delay. 5 to 180 ms
Customer Diagnostic Registers - Integer
| Registers | Name | Units | Access | Default | Description
| 0001, 0002 | DummyReg |  | Read-Only |  | Dummy register; always returns zero; can be used to scan for active MODBUS addresses
| 1701, 1702 | SerialNumber |  | Read-Only |  | The unique WattNode serial number
| 1703, 1704 | UptimeSecs | Seconds | Read-Only |  | Time in seconds since last power on
| 1705, 1706 | TotalSecs | Seconds | Read-Only |  | Total seconds of operation
| 1707 | Model |  | Read-Only |  | Encoded WattNode model
| 1708 | Version |  | Read-Only |  | Firmware version
| 1709 | Options |  | Read-Only |  | WattNode options
| 1710 | ErrorStatus | n.a. | Read/Write |  | List of recent errors and events
| 1711 | PowerFailCount |  | Read/Write |  | Power failure count
| 1712 | CrcErrorCount |  | Read/Write |  | Count of MODBUS CRC communication errors
| 1713 | FrameErrorCount |  | Read/Write |  | Count of MODBUS framing errors
| 1714 | PacketErrorCount |  | Read/Write |  | Count of bad MODBUS packets
| 1715 | OverrunCount |  | Read/Write |  | Count of MODBUS buffer overruns
| 1716 | ErrorStatus1 | n.a. | Read/Write |  | Newest error or event (0 = no errors)
| 1717 | ErrorStatus2 | n.a. | Read/Write |  | Next oldest error or event
| 1718 | ErrorStatus3 | n.a. | Read/Write |  | Next oldest error or event
| 1719 | ErrorStatus4 | n.a. | Read/Write |  | Next oldest error or event
| 1720 | ErrorStatus5 | n.a. | Read/Write |  | Next oldest error or event
| 1721 | ErrorStatus6 | n.a. | Read/Write |  | Next oldest error or event
| 1722 | ErrorStatus7 | n.a. | Read/Write |  | Next oldest error or event
| 1723 | ErrorStatus8 | n.a. | Read/Write |  | Oldest error or event
Note on E7: Before version 16, this was Read-Only
Note on E8: Before version 16, this was Read-Only
Note on E31: Before version 16, this was Read-Only
Note on E32: Before version 16, this was Read-Only
Note on E55: Before version 16, this was Read-Only
Note on E56: Before version 16, this was Read-Only
Note on E57: Before version 16, this was Read-Only
Note on E58: Before version 16, this was Read-Only
Note on E59: Before version 16, this was Read-Only
Note on E60: Before version 16, this was Read-Only
Note on E61: Before version 16, this was Read-Only
Note on E63: Before version 16, this was Read-Only
Note on E64: Before version 16, this was Read-Only
Note on E65: Before version 16, this was Read-Only
Note on E66: Before version 16, this was Read-Only
Note on E67: Before version 16, this was Read-Only
Note on E68: Before version 16, this was Read-Only
Note on E69: Before version 16, this was Read-Only
Note on E70: Before version 16, this was Read-Only
Note on E71: Before version 16, this was Read-Only
Note on E72: Before version 16, this was Read-Only
Note on E73: Before version 16, this was Read-Only
Note on B97: Register added on version 16
Note on B98: Register added on version 16
Note on B99: Register added on version 16
Note on E104: Before version 16, this was Read-Only
Note on E105: Before version 16, this was Read-Only
Note on E106: Before version 16, this was Read-Only
Note on E107: Before version 16, this was Read-Only
Note on E108: Before version 16, this was Read-Only
Note on E109: Before version 16, this was Read-Only
Note on E110: Before version 16, this was Read-Only
Note on E112: Before version 16, this was Read-Only
Note on E113: Before version 16, this was Read-Only
Note on E114: Before version 16, this was Read-Only
Note on E115: Before version 16, this was Read-Only
Note on E116: Before version 16, this was Read-Only
Note on E117: Before version 16, this was Read-Only
Note on E118: Before version 16, this was Read-Only
Note on E119: Before version 16, this was Read-Only
Note on E120: Before version 16, this was Read-Only
Note on E121: Before version 16, this was Read-Only
Note on E122: Before version 16, this was Read-Only
Note on B146: Register added on version 16
Note on B147: Register added on version 16
Note on B148: Register added on version 16
Note on B149: Register added on version 16
Note on E149: Can only be written when the IO pin is configured as an output (in modes 3 to 8)
Note on B150: Register added on version 16
Note on E155: On version 16, this assigns the same value to all 3 per-phase CtAmps registers when written. It reads zero unless all three per-phase CtAmps registers are the same, in which case it reads back that value.
Note on F156: Before version 16, this defaulted to zero.
Note on F157: Before version 16, this defaulted to zero.
Note on F158: Before version 16, this defaulted to zero.
Note on G171: Before version 16 only 0, 120 and 180 were allowed.
Note on B174: Register added on version 16
Note on B175: Register added on version 16
Note on B184: Register added on version 16